WiFi kit 2.0 MIM- H04EN Setup

Please check correct wiring schematic example below. Screened 2 core cable MUST be used for both R1 R2 and F1 F2 networks. This is to be earthed at one point only, with the screens joined in each outdoor unit.

In order to enable an indoor unit to communicate with this device, it must be told to do so. Installation option code 05 must be set to 1 for this. Please refer to the individual controller installation manuals for this. Full range available on our website www.GTPhelan.ie

If multiple systems are to be setup, the outdoor units should be addressed manually:

CAC- Press and hold K2 button.  ‘00AU’ should appear as below.

Change the address by short pressing the K2 button to the desired address. Press and hold K2 to save. System

FJM – Press and hold K2 button to enter the installation option menu. Press K1 to change SEG1 and SEG 2 until 04 appears (Channel address). Short press K2 to change the value from AU to the desired address. Press and hold K2 to save. System will now reset.

With all power on to all units and Wi-Fi module, press the SW3 button, on the inside of the Wi-Fi device. This will track the units connected.

Please ensure customer’s WiFi is working correctly and is in range of the WiFi module.

Using the customer’s phone, download the SMARTHINGS App and setup a Samsung account. Follow the App instructions and select air conditioner as the device to set up. Select ‘System Air Conditioner’ if available. Follow the on-screen instructions from here.

To add other users, an invite must be sent from this app, on this device.